Monitoring & Control equipment

- Level Sensor

### Scope

Level measurement shall be done by a low-maintenance submersible pressure sensor suitable for sewage water applications and for installation in the pump sump. The pressure sensor has to be connected to the RTU and should meet the following demands:

### Technical data

Output signal proportional to the level		4 – 20mA

Power supply 		10 – 30VDC

Pre-programmed measurement range		0-3m, 0-5m or 0-10m

0-9.8ft, 0-16.4ft or 0-32.8ft

Provided cable length		12m/39ft

Operational temperature range		-10 – 60°C or 14 – 140 °F

Long term instability 		< 0,1% FS per year

Calibration accuracy 						< 0,5% FS

Diaphragm			   				  SS 1.4404 AISI 316L

Heavy weight for little affect of turbulence		Yes

Soft cable for straight cable installation		Yes

Suitable for salt water installations		Yes

Part information printed on sensor body		Yes

Large diaphragm protection holes to prevent clogging		Yes

### Standards

In accordance with EN 61000-6-1:1999, EN 61000-6-2:1999,

EN 61000-6-3:2001, EN 61000-6-4:2001